## Electrodacus
Efficiency [%]	20%	Specifications:	0.7	KV-Number	Radagast		Extended Version			Electrodacus			Only input data on cells with this color.
Air density	1.2	V_Nomi	V/kRPM	Ri [ohm]	P_Nominal		Power Factor							Use [%]	0.53%	Wind-E
Number of E Gen	1	480	685.71	7.1	3000	W	0.87		Savonius Wind Turbine Calculator					Use [%]	2.64%	Turbine-E
Speed ratio	1	7.2km/h	10.8km/h	14.4km/h	18km/h	21.6km/h	25.2km/h	28.8km/h	32.4km/h	36km/h	39.6km/h	43.2km/h	46.8km/h	50.4km/h	54km/h	57.6km/h
Wind speed [m/s]	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16
Diameter [m] →	5	5	5	5	5	5	5	5	5	5	5	5	5	5	5	5
Height [m] →	6	6	6	6	6	6	6	6	6	6	6	6	6	6	6	6
T_period_ @1RPM	3.82	7.64	11.46	15.29	19.11	22.93	26.75	30.57	34.39	38.22	42.04	45.86	49.68	53.5	57.32	61.15
1	3.82	7.64	11.46	15.29	19.11	22.93	26.75	30.57	34.39	38.22	42.04	45.86	49.68	53.5	57.32	61.15
Gen speed RPM	3.82	7.64	11.46	15.29	19.11	22.93	26.75	30.57	34.39	38.22	42.04	45.86	49.68	53.5	57.32	61.15
Power Wind	18	144	486	1152	2250	3888	6174	9216	13122	18000	23958	31104	39546	49392	60750	73728
Tages-Wind %	1.40%	6.23%	11.34%	13.88%	13.92%	14.64%	10.21%	9.27%	6.19%	3.34%	3.08%	2.75%	1.17%	1.09%	0.37%	0.55%
Wind Energy / Wh/d	6.05	215.37	1322.38	3837.38	7517.93	13657.33	15125.95	20493.01	19490.77	14449.23	17687.73	20525.88	11122.36	12950.94	5383.85	9774
Turbine Power/W	3.6	28.8	97.2	230.4	450	777.6	1234.8	1843.2	2624.4	3600	4791.6	6220.8	7909.2	9878.4	12150	14745.6
Turbine Energy Wh/d	1.21	43.07	264.48	767.48	1503.59	2731.47	3025.19	4098.6	3898.15	2889.85	3537.55	4105.18	2224.47	2590.19	1076.77	1954.8
P_Generator/P_Nominal	0.03%	0.13%	0.29%	0.52%	0.81%	1.16%	1.58%	2.06%	2.61%	3.22%	3.90%	4.64%	5.45%	6.32%	7.25%	8.25%
Voltage @xRPM / V	2.62	5.24	7.86	10.48	13.1	15.72	18.34	20.96	23.59	26.21	28.83	31.45	34.07	36.69	39.31	41.93
I_actual / Ampère	0.37	0.74	1.11	1.48	1.85	2.21	2.58	2.95	3.32	3.69	4.06	4.43	4.8	5.17	5.54	5.91
Generator P_loss	436.85	109.21	48.54	27.3	17.47	12.13	8.92	6.83	5.39	4.37	3.61	3.03	2.58	2.23	1.94	1.71
Generator Power	0.84	3.37	7.57	13.46	21.04	30.29	41.23	53.86	68.16	84.15	101.82	121.17	142.21	164.93	189.34	215.42
P_All Generators	0.84	3.37	7.57	13.46	21.04	30.29	41.23	53.86	68.16	84.15	101.82	121.17	142.21	164.93	189.34	215.42
Output Power / W	0.84	3.37	7.57	13.46	21.04	30.29	41.23	53.86	68.16	84.15	101.82	121.17	142.21	164.93	189.34	215.42
Gen Energy / Wh/d	0.28	5.03	20.61	44.85	70.29	106.41	101.02	119.76	101.24	67.55	75.17	79.96	40	43.25	16.78	28.56
Generator active→	0	0	1	1	1	1	1	1	1	1
Extracted E / Wh/d / Harvest-Overview a Day / Ertrags-Tagesübersicht / Day-Wind velocity / Tages-Windgeschwindigkeit / Power/W & Energy/Wh/24h	0	0	20.61	44.85	70.29	106.41	101.02	119.76	101.24	67.55	75.17	79.96	40	43.25	16.78	28.56
																		Wind
																	KWh/Day	MWh / year
																	173.56	63.39
																	915.45	920.76
																	99.42%	Generator
																	Wh / Day	KWh / month
																	915.45	27.46
																	0.92KWh	/Day
																	W / h	MWh / year
																	38.14	0.33

																		Turbine
																	Wh / Day	KWh / month
																	34712.03	1041.36
																	34.71KWh	/Day
																	W / h	MWh / year
																	1446.33	12.68

## Wind
https://github.com/worlddevelopment/energy_through_airflow_vertical	Turbine- / Specifi- / cation: / ← ← ← |	Generator- / Specifi- / cation: / | → → →	1240	← KV / rpm/V / Revolutions/minute / that are required to / generate exactly 1V.	Kt / Nm/A→ / Torque constant, / i.e. torque / 1A / current.	0.0242	Wind Power Calculator					By / Electrodacus / & / Faerietree (J.R.I.B.-Wein)	INPUT FIELDS / Only input data on cells with this color.
Average / Turbine Efficiency / %	20%	Use self-excitated! / e.g. permanent magnets. / #Generators =	TODO: Use peak Voltage/Back EMF isntead of RMS voltage for bushless / 3phase. May depend on motor type? / V/RPM	Ri / ohm	P_Nominal / W	V_Nomin. / V	Power Factor / Motor plate or figure out, e.g. measure.	Idle Current / I_0 / A	CC-BY-SA Licence (SA = share alike)					UseW/%=	15.69%	Wind-E
Site air density / kg/m^3= / (e.g. 1.225 @ 0m height @15°C temp.)	1.23	1	0.31	7.1	3000	380	0.87	0.9	Use, share, give credit! And / share improvements with the planet.For a better world.					UseT/%=	77.53%	Turbine-E	V_Wind_ideal	V_Wind_critical
Ratio V_Rotorarmtip / V_Wind / Tip Speed Ratio (TSR)	1	7.2km/h	10.8km/h	14.4km/h	18km/h	21.6km/h	25.2km/h	28.8km/h	32.4km/h	36km/h	39.6km/h	43.2km/h	46.8km/h	50.4km/h	54km/h	57.6km/h	31.16km/h	34.28km/h	Note: TSR Tip speed ratio Depends on how much / wind the turbine catches and transforms into kinetic / energy, i.e.speed.
Wind speed / m/s	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	8.66	9.52
Diameter_Turbine / m =	4	4	4	4	4	4	4	4	4	4	4	4	4	4	4	4	4	4
Area_Turbine_in_Wind / m =	24	24	24	24	24	24	24	24	24	24	24	24	24	24	24	24	24	24
T_period_turbine / s (time/revolution)	12.57	6.28	4.19	3.14	2.51	2.09	1.8	1.57	1.4	1.26	1.14	1.05	0.97	0.9	0.84	0.79	1.45	1.32
30 ←Ratio Transm.Gen./Turb. | @1:1→	4.77	9.55	14.32	19.1	23.87	28.65	33.42	38.2	42.97	47.75	52.52	57.3	62.07	66.85	71.62	76.39	41.33	45.47
Generator Revolutio/min (rpm)	143.24	286.48	429.72	572.96	716.2	859.44	1002.68	1145.92	1289.16	1432.39	1575.63	1718.87	1862.11	2005.35	2148.59	2291.83	1240	1364
Power Wind	14.7	117.6	396.9	940.8	1837.5	3175.2	5042.1	7526.4	10716.3	14700	19565.7	25401.6	32295.9	40336.8	49612.5	60211.2
Day-Wind-Distrib. (=>6m/s)	1.40%	6.23%	11.34%	13.88%	13.99%	13.64%	10.21%	9.27%	6.19%	3.34%	3.08%	2.75%	1.17%	1.09%	0.37%	0.50%	= 98.44%	← Total Wind / % / 24h
Wind Energy / Wh/d	4.94	175.88	1079.95	3133.86	6169.59	10391.44	12352.86	16735.96	15917.46	11800.21	14444.98	16762.8	9083.26	10576.6	4396.81	7259.56
Turbine Power / W	2.94	23.52	79.38	188.16	367.5	635.04	1008.42	1505.28	2143.26	2940	3913.14	5080.32	6459.18	8067.36	9922.5	12042.24
Turbine Energy / Wh/d	0.99	35.18	215.99	626.77	1233.92	2078.29	2470.57	3347.19	3183.49	2360.04	2889	3352.56	1816.65	2115.32	879.36	1451.91		V_still_safe_to_operate_generate_at = V_Nominal/Design + delta V_margin
Voltage @xRPM / V	43.9	87.79	131.69	175.58	219.48	263.38	307.27	351.17	395.06	438.96	482.86	526.75	570.65	614.54	658.44	702.34	380	418
I_actual / Ampère ← wrong!? It's AC. TODO Include power factor and figure proper formula, include RMS, sqrt(3)?	6.18	12.37	18.55	24.73	30.91	37.1	43.28	49.46	55.64	61.83	68.01	74.19	80.37	86.56	92.74	98.92	53.52	58.87
Torque / Nm	0.15	0.3	0.45	0.6	0.75	0.9	1.05	1.2	1.35	1.5	1.65	1.79	1.94	2.09	2.24	2.39	1.29	1.42
Generator Efficiency eta_max =	0.38	0.53	0.61	0.65	0.69	0.71	0.73	0.75	0.76	0.77	0.78	0.79	0.8	0.81	0.81	0.82	P_ohmic_loss @constant power / NOT THE CASE HERE!.	Formula only works if Power is kept constant as then U_0 can be factored in. Else losses just depend on current, see below.	0.01	P_loss = P_0 / U_0^2 not working here due to power not being kept constant!?
Generator P_ohmic_loss / (@high current, load dependent)	271.39	1085.55	2442.49	4342.21	6784.7	9769.97	13298.02	17368.84	21982.43	27138.81	32837.96	39079.88	45864.58	53192.06	61062.32	69475.35	20338.03	24609.01
Generator P_iron_loss if iron core / (@I_0, i.e. low current, often at low speed, load independent)	39.51	79.01	118.52	158.03	197.53	237.04	276.54	316.05	355.56	395.06	434.57	474.08	513.58	553.09	592.6	632.1	=> Due to i_0 also pulling efficiency to zero at low currents while r_i pulls down / at high currents, the peak efficiency will be inbetween (see eta_max above).
P_Generator/P_Nominal	9.05%	36.19%	81.42%	144.74%	226.16%	325.67%	443.27%	578.96%	732.75%	904.63%	1094.60%	1302.66%	1528.82%	1773.07%	2035.41%	2315.84%	← Auslastung / Generator capacity usage. Red is only tolerable to a certain degree. At some point the mechanic will break, even if the rotor is electrically/mechanically deccelerated to not go over the rated RPM.
Generator Power / W	236.11	944.43	2124.97	3000	3000	3000	3000	3000	3000	3000	3000	3000	3000	3000	3000	3000	← Assumes the generator is prevented to generate more than its design power. (see red alert background in the power / power_nominal ratio above)
P_All Generators / W	236.11	944.43	2124.97	3000	3000	3000	3000	3000	3000	3000	3000	3000	3000	3000	3000	3000	Gen.Tolerated Min.Efficiency:
Output Power / W	2.94	23.52	79.38	188.16	367.5	635.04	1008.42	1505.28	2143.26	2940	3000	3000	3000	3000	3000	3000	Efficiency eta_min_tolerated =	0.5
Gen. Energy / Wh/d	0.99	35.18	215.99	626.77	1233.92	2078.29	2470.57	3347.19	3183.49	2360.04	2214.84	1979.73	843.75	786.62	265.87	361.7	Gen.Theo.Max.Efficiency:
Generator active cut in / off	0	0	0	1	1	1	1	1	1	1	1	Efficiency eta_max =	0.76
Extracted E / Wh/d	0	0	0	626.77	1233.92	2078.29	2470.57	3347.19	3183.49	2360.04	2214.84	1979.73	843.75	786.62	265.87	361.7	I_@eta_max =	6.94	A
ONLY CONSTRUCT A WIND POWER PLANT IF YOU HAVE HIGH WINDS! IT'S NOT A MIRACLE MACHINE. NO WIND => NO POWER OUTPUT!
ONLY CONSTRUCT A HYDRO POWER PLANT IF YOU HAVE EITHER HIGH HEIGHT DIFFERENCE (head) OR HIGH FLOW (water masses)! KEEP WAY FOR FISH IN BOTH DIRECTIONS (up- and downstream).
OFTEN A SIMPLE CROSS-FLOW TURBINE PRODUCES MORE AVERAGE OUTPUT IF VARIABLES LIKE FLOW RATE VARY A LOT OVER YEAR,WATER FLOW RATE AS ITS EFFICIENCY REMAINS STABLE OVER A WIDE RANGE (contrary to some others, e.g. pelton is sensible to too much water while turgo turbine isn't so much). ESPECIALLY IF NEITHER AVAILABLE HEAD NOR FLOW RATE ARE CONVINCING/HIGH ENOUGH.
IT'S GOOD TO GET AN IDEA OF HOW MUCH ENERGY YOU CAN GET AND TO TEST ELECTRONICS PRINCIPLES. LATER YOU CAN STILL CONSTRUCT THE PENSTOCK WITH THE 30m HEAD PELTON OR DIRECT DRIVE TURGO TURBINE. OR THE HIGH WATER MASSES FRANCIS TURBINE OR KAPLAN TURBINE. OR VORTEX OR WHATEVER OTHER TURBINE YOU WANT TO TEST. DON'T EXCEPT MIRACLES THOUGH AND KEEP US INFORMED ABOUT RESULTS OF EXPERIMENTS AS WE DO TOO!

																		Wind
																	KWh/Day	MWh / year
																	140.29	51.24
																	21752.8	22004.95
																	98.85%	Generator
																	Wh / Day	KWh / month
																	21752.8	652.58
																	21.75KWh	/Day
																	W / h	MWh / year
																	906.37	7.95

																		Turbine
																	Wh / Day	KWh / month
																	28057.23	841.72
																	28.06KWh	/Day
																	W / h	MWh / year
																	1169.05	10.25

Harvest-Overview a Day / Ertrags-Tagesübersicht / Day-Wind velocity / Tages-Windgeschwindigkeit / Power/W & Energy/Wh/24h
Energy: Wind vs. Turbine vs. Extracted
Harvest-Overview a Day / Ertrags-Tagesübersicht
Wind velocity / Windgeschwindigkeit (distributed / day) / m/s
Logarithmic Base 10 Power/W & Energy/Wh/24h
Harvest-Overview a Day / Ertrags-Tagesübersicht
Wind velocity / Windgeschwindigkeit (distributed / day) / m/s
Power/W & Energy/Wh/24h
Harvest-Overview a Day / Ertrags-Tagesübersicht
Wind velocity / Windgeschwindigkeit (distributed / day) / m/s
Power/W & Energy/Wh/24h
Harvest-Overview a Day / Ertrags-Tagesübersicht
Wind velocity / Windgeschwindigkeit (distributed / day) / m/s
Power/W & Energy/Wh/24h

## Motor
Axial Flux Motor Design
Motor:
Motor radius/m =	0.2500	=>Motor circumverence/m =	1.5708
		=>Motor area/m^2 =	0.1963	BUILD THE MILL!

Rotor:
Pole location radius/m =	0.1667	=>Pole location circumverence/m =	1.0472	← Assumes the poles are placed at 2/3 * radius.
Pole spacing/m =	0.0100					#poles_optimum=		Pole width/m_optimum =

EITHER:	the higher the greater the 'reduction' => more torque
Rotor Pole count =	20	=>#pole pairs =	10	=>#pole gaps =	20
		=> Pole width/m =	0.0424	← Note the pole height as high as possible because mostly the radial components contribute to the torque. → compromise: e.g. oval. Though if thinking of a generator then better circular to ease current induction?, see Lebowski's explanation endlesssphere.
OR: (Attention, pole spacing not considered!! As it required iterating to solve.)
Pole width/m =	0.0500
		=> Rotor Pole count =	16.94	=>#pole pairs =	8.47
		Must be multiple of 2! (only pairs!)

f_modulation / Hz =	20000.000
f_AC_max / Hz =	75	=>Revolutions/s =	7.50	<=> Rpm_max =	450
f_AC_target / Hz =	50	=>Revolutions/s =	5.00	<=> Rpm =	300
f_AC_min / Hz =	25	=>Revolutions/s =	2.50	<=> Rpm_min =	150

Stator:
Stator winding/teeth count =	9	← Only multiples of phase count! e.g. x * 3 if 3 phases!
Stator thickness (windings flush) /m =	0.0200	NOTE: The rotor magnets must be contained within the outer bounds of the stator windings to fully utilize the magnetic flux!
EITHER:
#Turns / Winding =	27
#Parallel wound/ Multiplier =	2	=> #Turns / Winding =	54	=> Voltage / V_DC =
		EITHER:
		Diameter_magnet_wire / m =	0.0010	=> Current / A =
				=> Volume used / m^3 =		=> Radius used / m =
		OR:
		Calculate magnet wire diameter from space and current constraints.

OR:
Target voltage / V_DC =	700
Target amperage / A =	10
		TODO if useful.